## Sheet1
Type | CT size | Devices | Wire Diameter
NCTK-2030 250A/5A 1 1.25VA | 20mm*30mm | CHS2、C6 | 250A/5A *3；Wire diameter (copper wire) ≤120 mm²
NCTK-4060 500A/5A 0.5 2.5VA | 40mm*60mm | CHS2、C6 | 500A/5A *3；Wire diameter (copper wire)≤300 mm²
NCTK-50100 1000A/5A 0.5 5VA | 50mm*100mm | CHS2、C6 | 1000A/5A *3；Wire diameter (copper wire)≤800 mm²
NCTK-60125 2000A/5A 0.5 10VA | 60mm*120mm | CHS2、C6 | 2000A/5A *3；Double or multi-spliced cables are used for currents above 1000A. The CT should be selected according to the actual total outer diameter of the cable, and the aperture should be 60mm*120mm.